## Slide 1: US29441
Demonstrate and apply knowledge of cable coding, colours, characteristics, applications, and capacity

## Slide 2: Cables
What’s the size of cable we use for:
Lighting circuits
          Domestic?
          Commercial?
Power circuits
          Domestic?
          Commercial?

## Slide 3: Selecting correct cables is one of the most important aspects of your work. Cables, when correctly selected and installed, ensure a safe, durable and efficient electrical system.
The information you need to correctly select cables, is contained in:
 AS/NZS 3000:2007, Incorporating Amendment No.1 and No 2,
 AS/NZS 3008.1.2:2010, and
 Manufacturers’ catalogues and guides.
Please obtain AS/NZS 3000 and 3008 before working through this module

## Slide 4: Materials Used in Cables
Conductor materials: Four conductors commonly used in cables are:
stranded copper
solid copper (drawn)
stranded aluminium
solid aluminium (less conductive, about 60% of that of copper)

## Slide 5: Materials Used in Cables
Cable and Flexible Cord Insulating Materials
Insulation needs to be a material that has high electrical resistance.
The most common materials used for insulation in cables and flexible cords are:
 Plastics:
1- Thermoplastics: Become soft when warmed and harden again when cooled. The process is repeatable. That are of interest to us are polyvinyl chloride (PVC) and polyethylene (PE). TPS is a PVC cable operating temp: 0-60C
2- Thermosetting plastics: Thermosetting plastics undergo a chemical change when they are subjected to heat and pressure and cannot be re-plasticised by further heat and pressure. cross-linked polyethylene XLPE withstands up to 90C
Rubber and synthetic rubber Examples of common types are:
 60°C rubber (vulcanised rubber, for flexible cables only)
 85°C rubber (butyl rubber)
 150°C rubber (silicon rubber).
Ethylene propylene rubber (EPR) is synthetic, and has physical and electrical properties superior to, butyl rubber.
(MIMS) mineral (magnesium oxide) (non-flexible) insultions: fire resistance and heating elements
Paper insulation: used for high voltage cables and transformers

## Slide 6: Physical and Electrical Data Guide to Materials’ Performance page 8 , 9 & 10 of US29441

## Slide 7
Armouring, Sheathing and Screening Materials
All cables must be protected against any risk of mechanical damage that is liable to occur under normal conditions of service.
Sheathing provides the first line of protection. Range of protection (depending on the material used) in terms of smoke/acid emission, toxic gas emission, flame propagation, flexibility, and resistance to heat, cold, fluid and abrasions.
Further protection may include enclosing sheathed cables in trunking, ducting or conduit.
However, it is often more convenient to use armouring to provide further mechanical protection. Steel wire is the most common method used but steel tape armour and aluminium strip may also be used.
Metallic armours and sheaths of cables must be earthed. They may be used as protective earthing conductors if requirements are met. These requirements are that;
 the armouring or sheathing is used as an earth-continuity conductor only to protect its associated conductors and apparatus.
 its conductance must be adequate for the purpose.
 joints must be sound and protected against corrosion.

## Slide 8: Identifying Different Types of Cable Many cables are known by their abbreviations and initials, which describe the makeup of each layer from the inside to the outside. The following are most common: (page 11)

## Slide 9
Determining Cable Conductor Size
Conductor size can be determined by viewing on the cable sheathing, or the cable manufacturer’s labels on the cable drum reel or boxes. You can also determine the size of a cable conductor by measurement using a micrometer and checking the conductor size next to the cable manufacturer’s cable data.
(page 12)

## Slide 10
Features of Common Cables
Common cables that we use have various features These cables are:
 PVC insulated cables
 XLPE insulated cables
 mineral insulated cables.
(Page 18)

## Slide 11
Flexible Cables and Cords
The only difference between a flexible cable and a flexible cord, is the size of the conductor or conductors.
Flexible cable consists of one or more conductors. The diameter of the wires is greater than 4 mm2, but flexible.
Flexible cord has the cross-sectional area of not exceeding 4 mm2.
The diameter of the strands varies from 0.21 mm to 0.31 mm,
The number of copper strands in each conductor is usually 23 or 40.
A conductor and its insulation are called a core.

## Slide 12
Types of Flexible Cord
Flexible cords are available in many types and sizes. The figure below shows some of the more common varieties and their uses.
(Page20)

## Slide 13: Conductor Colours
Identification AS/NZS 3000:2007 Section 3.8.1
Where identification is achieved using the colour of the conductor insulation, the colours specified in AS/NZS 3000:2007, Table 3.4 shall be used.
Sleeving may be used for colour identification, by sleeving using colours corresponding to those listed above and at each, and every termination for the following purposes:
 conductors with black or light blue insulation used as active conductors; or
 conductors with any colour other than green, yellow, green/yellow, black or light blue insulation used as neutral conductors; or
 conductors in multi-core cables with any colour other than green, yellow or green/yellow insulation used as earthing conductors.

## Slide 14
Exceptions 1
Protective earthing (PEC) and equipotential (EQB) conductors do not need to be coloured green/yellow in the following situations:
 When a bare or aerial conductor used as PEC
 Where a suitable screen of a multi-core cable is used as (PEC)
 When an insulated protective earthing conductor is not normally manufactured in the green/yellow colour combination, e.g. silicon compounds.
In installations such as these, the use of sleeving at terminations is recommended wherever it is not obvious that the conductor is being used for earthing purposes.

## Slide 15
Exceptions 2
An active or neutral conductor does not need to be coloured in accordance with the colours permitted by Table 3.4 when:
 insulated conductors in a multi-core flexible cable have each core clearly identified by means of numbering, lettering or equivalent means;
 or conductors of flexible cords and cables are identified by alternative colours in accordance with AS/NZS 3000:2007, Clause 3.8.3.3; or
 insulated aerial conductors are identified by several small longitudinal ribs around the circumference, the neutral conductor shall be identified by multiple longitudinal ribs evenly spaced around the entire circumference and length of the conductor that clearly distinguish it from the other conductors.
AS/NZS 3000:2007, Clause 3.8.3.3 specifies European cable identification c

## Slide 16
The table below shows the coordination of conductor insulation colours of single-phase cables manufactured to current and superseded AS/NZS standards.
This includes flexible cords and cables
Note:
1. The neutral core may or may not be included in a multi-core cable or cord.
2. The European active colour for multiphase cables and cords for all phases is brown.
3. Care should be taken with imported equipment that does not use AS/NZS colour codes.
Test to make sure first.

## Slide 17
Manufacturer’s Data
Information about the construction of a cable can be found in its abbreviated name.
The components of the name refer to the components of the cable in the order.
For example, consider the following:
6 x 16mm2 copper conductors, PVC, PVC, SWA, PVC

## Slide 18: Factors affecting the selection of cables
Basic Cable Requirements
A cable must be able to carry electrical energy efficiently and safely from the supply source to the load.
The cable’s conductors and insulation should not deteriorate with age, and the sheath of the cable must adequately protect the conductors and the insulation it surrounds from mechanical damage, chemical attack, high external temperatures and moisture.
The heat generated in cable conductors must be limited to within the maximum working temperature of the conductor insulation as specified by the manufacturer.
To ensure the correct voltage and current are supplied by a cable, you must consider the following factors when selecting the cable:
 The current rating of the cable IN (And also the PSC of the circuit).
 The voltage drop along the cable (length of run).
 The class of excess-current protection used (Type A, B, C MCB).
 The ambient temperature (Environnemental conditions).
 Installation methods (Earthing requirements and mechanical factors).
 Derating factor. (1Φ, 3Φ, temperature etc.).

## Slide 19
Cable Current Rating
The current rating for cables, is the highest RMS current that can be carried under specified conditions by a cable conductor without the insulation temperature limit being exceeded
Current carrying capacities (CCC) of PVC
Insulated and PVC sheathed single phase
two core and earth cables, un-armoured
CCC of PVC insulated and PVC sheathed
three phase three core and earth cables,
un-armoured

## Slide 20
Using AS/NZS 3008 for Cable Calculations
The tables in AS/NZS 3008 set out the CCC, the method of installation, and the environmental conditions under which the cable can be used.
They also give the current ratings of various cables used in specified conditions.

## Slide 21
Voltage Drop
The degree of voltage drop depends on the:
 conductor material (resistivity)
 cross-sectional area of the conductor
 route length of the conductor
 amount of current flowing in the conductor.
According to AS/NZS 3000
The voltage drop between the point of supply for the low voltage installation, and any point in that electrical installation (final point in any sub-circuit) does not exceed 5%
Unless an installation is specifically designed to take account of a specific volt drop, the wiring to all low voltage supply points (sub-circuits) shall ensure that the drop in voltage shall not exceed 2.5% of the standard voltage.

## Slide 22: Route length is discussed in AS/NZS 3000:2007: Appendix B: Table B1

## Slide 23
Determining minimum cable size based on voltage drop
To satisfy the voltage drop limitations of a circuit, it is necessary to determine the:
 current (I) requirements of the circuit
 route length (L) of the circuit
 maximum voltage drop (v.d.) permitted on the circuit run.
Lets work out the actual volt drop of a circuit:
If a 3 phase cable carrying 6 A over a distance of 20 meters having Vc= 35mV/A.m. What will be the Vd along its length?
Vd = actual voltage drop of the circuit
Vc = the millivolts (volts/1000) per ampere per meterroute length of circuit in millivolts per ampere metre (mV/A.m) AS/NZs3008, tables 40 and 50
L = route length of circuit, in metres
I = the current to be carried by the cable, in amperes.

## Slide 24
Example 1
A single-phase 230 V 15 A circuit with close protection is to be run 25 meters. You would like to use a 2.5 mm2 TPS, 75C cable and underground (not clip it to a wall). Column 25 (not 2) in Table 4 gives a current rating of 34 A for this cable, which is adequate for this circuit. Remember as a rule-of-thumb that the maximum Vd for 230 V is 5.75 V.
Why table? Because it’s single phase
You would calculate the Vd as follows:
Table 42 gives a Vc (not Vd) value of 15.6 millivolts per ampere per meter for this cable.
This Vd exceeds the maximum of 5.75 volts for this 230V circuit. Therefore, this size of cable
is unsuitable. Therefore we must select a larger cross-sectional area and hence, a lower Vd value.

## Slide 25
Students’ class work
The table shows that the next larger sized cable is 4 mm2, and the Vc given in Table 42 is 9.71 millivolts per ampere per metre
Vd= 4.2
This value is below the maximum of 5.75V, and so your choice of cable is 4mm2 twin TPS.
Example 2
Using the details in the above example, what sized three-core cable would you use to deliver a 400 V 15 A balanced three-phase supply with close protection to a sub-board 25 meters away? Cable is 75C unenclosed but fixed to a surface

## Slide 26
Example 3
Using the details in the above example, what sized three-core cable would you use to deliver a 400 V 15 A balanced three-phase supply with close protection to a sub-board 25 meters away? Cable is 75OC unenclosed but fixed to a surface, allow 20% allowance for load growth. If the ambient temperature is 25C
a) Calculate the maximum demand current of the installation before the allowance for growth.
b) Calculate the current demand after the allowance for load growth required. Please show workings.
c) What size of cable would satisfy this current demand?
d) What is the value of de-rating factor for the ambient temperature?
De-rating factor? CCC x rating factor = 25 x 1.06 = 26.5A
AS/NZs3008 page 88
Table 27.1 for Air and concrete slabs
Table 27.2 for under ground cables

## Slide 27
Cable Selection Example (page 32)
A three-phase, 400V, copper, mains cable is being installed in an electrical installation comprising 4 houses, a milking shed and out-buildings.
Use the following information and information from AS/NZS3008 to calculate the size of cable required.
Installation information
 Installation Route: 50m length between the point of supply and the main switchboard
 Installation Method: Buried direct
 Maximum Demand: 70kW balanced over the three phases
 Voltage Drop: Maximum permitted voltage drop is 1.5%
 Growth Allowance: An allowance of 15% for load growth
 Environment: The ambient soil temperature is 20oC
 Conductor Supplier Information: Conductor temperature of 75oC
 Indicate the correct answer for each section. Show workings where applicable.

## Slide 28
a) Calculate the maximum demand current of the installation before the allowance for growth.
b) Calculate the current demand after the allowance for load growth required. Please show workings.
c) What size of cable would satisfy this current demand?
d) What is the value of de-rating factor for the ambient temperature?
De-rating factor? CCC x rating factor
AS/NZs3008 page 88
Table 27.1 for Air and concrete slabs
Table 27.2 for under ground cables
e) What is the volt drop within the percentage allowed?
1.5% of 400V=6v

## Slide 29
Calculate the minimum Vc=mV/A.m allowed:
Vc=
We now need to look at Table 42 (Page 110), column 6, to find a cable size that has a value smaller than this
The 25mm2 cable that satisfies the current carrying capacity has a Vc value of 1.54 and so this is not low enough. The cable size that has a Vc value less than 1.032702 is 50mm2 and so this would have to be used.

## Slide 30
De-rating factors
AS/NZs3008 Page 79-88
Table 22 for single or multi core bunched or grouped circuits
Table 23 for single core in cable support in air (e.g. Cable tray)
Table 24 for multi core in cable support in air (e.g. Cable tray)
Table 25?
Table 26?
Table 27.1 for Air and concrete slabs
Table 27.2 for under ground cables

## Slide 32
Harmonic Currents and Cable Current Carrying Capacity
Non-linear loads generate harmonics in line currents, resulting in additional conductor heating.
Non-linear loads are solid-state energy conversion devices, traction drives industrial variable speed drives, and arc welding equipment.
To include the effects of harmonics, the frequency spectrum of the load, has to be known.
Harmonics generated by non-linear loads decrease the quality of power supplied and cause a de-rating of the cable due to the increased load current.
A load draws 40A current, however if 20% harmonics is presented then a reduction factor of 0.86 is applied and the design load becomes: 40/0.86 =47A so higher conductor will be required

## Slide 33
Short Circuit Performance
Short circuit currents increase the current on the cable dramatically. This increases the cable temperature to a point where it may exceed the permissible maximum temperature
The minimum cable size for a given type of cable due to short circuit temperature rise is typically calculated with an equation of the form:
Where:
S = cross-sectional area of the cable (mm2)
I = the prospective short circuit current (A)
t = the duration of the short circuit (s)
k = the short circuit temperature rise constant

## Slide 34
The constant k can be found from table 52 of AS/NZS3008 using the initial temperature and final temperature

## Slide 35
Example
Determine, using the adiabatic equation, the minimum size of conductor for the following.
 70C Thermoplastic, PVC cable
 Temperature rise to 160C which gives k = 115
 Fault current of 18779A
 Disconnection time of 1.5 seconds
A cable greater than 200mm2 would be adequate for this situation

## Slide 36
Earth Fault Loop and cable size
To fulfil this requirement of AS/NZS 3000, when a fault occurs, the impedance of the fault current path (referred to in the Wiring Rules as the Fault Loop Impedance Path) must be low enough to allow sufficient current to flow to ensure the protective device will operate within the specified time

## Slide 37
The actual value Zin is calculated using:
Zin = Ze + (R1 + R2)
Maximum earth fault loop impedance
The maximum value Zs is calculated using: 𝒁s=𝑼o/Ia
Where:
Zs = Maximum earth fault loop impedance
Uo = Nominal phase voltage
Ia = Current ensuring automatic operation of the protective device
Ia for circuit is the mean tripping current as follows:
Type B = 4 x rated current
Type C = 7.5 x rated current
Type D = 12.5 x rated current
The value of Zs may be used to calculate the appropriate earth cable size in terms of AS/NZS 3000: Section 5.7.4. However, Table 8.1 in AS/NZS 3000 provides these values.

## Slide 38
Maximum Demand
The cable size chosen for an installation doesn’t have to be able to carry the full loading of everything supplied. This is because it is assumed that not all appliances, lights, heating and cooking appliances will be used at the same time.
Table C1 of AS/NZS 3000:2007 sets out the maximum demand factors for single and multiple domestic electrical installations. AS/NZS 3000: Clause 2.2.2, states that maximum demand current can be determined by one of four methods—calculation, assessment, measurement or limitation.

## Slide 40
Let’s look at an installation with the following loads
 30 points of lighting
 1250W of outdoor lighting
 25 x 10A socket outlets
 2kW cooking appliances
 1kW of space heating
 1.5kW instantaneous water heater
You will need to refer to Table C1 of AS/NZS 3000:2007 for the following explanation
Answers page56 onwards

## Slide 41
Calculation of Maximum demand-Example 2
A 1 phase domestic installation has the following loads:-
23 Light points
2 numbers 15 A Socket outlets
6 single socket outlets
10 double socket outlets
Cooking Range 10 kW
Hot water controlled 4.8 kW
4 Flood lights 300 W each

## Slide 42
Equipment | Number of points | Load group | Calculation | Load current
Lighting points |  |  |  | 
300W flood lights Outdoor Lighting |  |  |  | 
Single socket outlets |  |  |  | 
Double Socket Outlets |  |  |  | 
15 A Socket outlets |  |  |  | 
Cooking Range 10 KW |  |  |  | 
Controlled Hot water Heater 4.8 KW |  |  |  | 
 |  |  | Max. Current Demand | 

## Slide 43
Equipment | Number of points | Load group | Calculation | Load current
Lighting points | 23 | A(1) | 1 to 20=3A 21-40 3=2A | 5A
300W flood lights Outdoor Lighting | 4 | A2 | 1200x0.75/230 | 3.9A
Single socket outlets | 6 | B1 | For additional 21 to 40= 5A 6 points additional | Added bellow
Double Socket Outlets | Change to single 10 x 2= 20 | B1 | 1-20= 10A+ 5A | 15A
15 A Socket outlets | 2 | B3 | 10A | 10A
Cooking Range 10 KW | 1 | C | 10x1000x0.5/230 | 21.7A
Controlled Hot water Heater 4.8 KW | 1 | F | 4.8x1000/230= | 20.9A
 |  |  | Max. Current Demand | 77A